## Slide 1: MODULE 8 Metering Considerations

## Slide 2: M&V, Step by Step
Plan
Measure and collect data
Develop baseline model
Measure and collect data
Report
Adjust baseline model
Installation of ECM

## Slide 3: Learning Objectives
Define key terms: metrologist, metrology, calibration, in-use calibration check
List commonly measured parameters in M&V activities
Characterize the different types and uses of metering systems
Articulate best practices for reducing uncertainty in the measurement, logging, communication, storage, calculation, and stipulation of metering data
Discuss the need for the calibration of metering system components as well as safety and cost concerns relevant to metering

## Slide 4: The Importance of Metering
Metering is at the core of M&V.
Without the data collected through metering, M&V is nothing more than guesswork or hocus-pocus.

## Slide 5: What Can Be Measured?
Most energy use measurement performed for M&V purposes is of electricity.
Even so, a wide array of energy systems, sources, and carriers can be influenced by an ECM, including:
  Diesel
  Steam
  Geothermal energy
  Coal
  Gas

## Slide 6: Parameters for Measurement
Once the energy use has been identified for measurement, parameters influencing the energy use may need to be measured as well.
Of these parameters, temperature, flow, and production are arguably the most common.
Other examples of relevant parameters include production, quality of materials, concentration of elements in materials, load, human behavior, equipment condition, humidity, illuminance (lux), and location.

## Slide 7: Combining Parameters
Sometimes parameters must be combined to form relevant data.
Example: Thermal energy, typically composed of the flow of the energy carrier and the temperature difference of that carrier through a process.

## Slide 8: Methods of Measurement
Indirect
Direct measurements with a bucket and stopwatch used to derive volumetric flow rate.
Measurements can be taken directly or indirectly, with or without equipment.
Direct
A count of the number of apples washed (without equipment)
A laser that, when tripped, counts the number of washed apples on a conveyer belt (with equipment)
Notes: Instructor Note: The most common measurement in M&V contexts is of energy or resource use. This is the direct measurement of the consumption of a resource that enables the delivery or existence of a service—e.g., burning fuel to drive to the beach or coal to illuminate street lamps.

## Slide 9: Types of Metering Systems
Metering systems can be categorized in different ways. They may be either permanent or portable (or temporary). They may also be distinguished by their data communication capabilities:
  Hardline data communication capabilities
  Wireless data communication capabilities
  No data communication capabilities—internal storage or instantaneous readings only

## Slide 10: Metering Systems
Permanent
Cannot be removed without disrupting energy, resource, service, or product supply
Protected against environment
Usually transmit data through hardline or wireless communication systems
Bulky
Credit under GreenStar/ Energy Star. ISO 14001. ESG LEED(?)
Portable or Temporary
Lightweight and portable
Usually battery powered, or with battery backup
Non-intrusive sensors (don’t impede the normal operation of what is being measured)
Usually less accurate
Can be expensive

## Slide 11: Types of Portable Metering Systems
Two basic subtypes of portable metering systems:
  Handheld instantaneous metering
  Metering with data logging
The latter either have no data communication capabilities or communicate data through an internet or mobile network.

## Slide 12: Which Type of Metering to Use?
Use a handheld instantaneous metering system when verification of existing or temporary metering data is required or when developing the requirements for a new permanent or temporary meter.
Use permanent metering when performance assessment is expected to take place over the course of six or more months.
Use metering with hardline communication capabilities when the environment is unsuitable for or not conducive to mobile or other wireless communication protocols.
Notes: Instructor Note: All non-instantaneous metering systems should have backup power and internal data storage to minimize the risk of power or communication loss. Also, be aware that metering systems with internal data storage but no data communication capabilities have a tendency to lose data after a period of about two weeks.
When in doubt, consult the project’s metrologist for a better understanding of metering requirements, setup, and conditions. Metrology is a distinct field of specialization, so if you’re unsure, don’t be afraid to ask for help.

## Slide 13: Accuracy and Credibility
As noted in Module 1, an appropriate balance must be achieved between the reduction of uncertainty through metering and the cost of metering.
When trying to strike this balance, the CMVP must consider the impact of uncertainty on the M&V process as a whole.
With the right balance, stakeholders will be aware of and in agreement about acceptable levels of uncertainty. This can help minimize finger-pointing if results are not as expected.

## Slide 14: Sources of Uncertainty
Common sources of uncertainty in M&V data relate to:
  Measurement
  Logging
  Communication
  Storage
  Calculation
  Stipulation
Notes: Instructor Note: A stipulation is “an assumption on which rests the validity or effect of something else.”

## Slide 15: Data Measurement Best Practices
To improve data credibility and reduce uncertainty:
  Use the most appropriate type of sensor for the task
  Check the minimum and maximum range of measurement required and choose the sensor accordingly
  Ensure proper installation and fit of sensor by following the manufacturer’s requirements
  Protect against tampering and the elements
  Perform routine calibration checks
Notes: Instructor Notes
Provide examples of each bullet:
Appropriate Type – Flow meters: https://instrumentationtools.com/difference-invasive-non-invasive-intrusive-non-intrusive/
Range/Size: https://www.flex-core.com/products/current-transformers/?gclid=CjwKCAjww7KmBhAyEiwA5-PUSvd6T5keNyT6pkOeSYtBM-QDjQbzYiC9GY706n3R7iAVdreXs7M5hhoC-bwQAvD_BwE
Thermocoupler: https://www.omega.com/en-us/temperature-measurement/temperature-wire-and-cable/c/thermocouple-wires?GUID=7018W000000X7vBQAS
https://www.emerson.com/en-us/automation/measurement-instrumentation

## Slide 16: Data Privacy/Ownership
Identify issues.
Ensure access and rights to use.
Understand data anonymization: “removing personally identifiable information from data sets, so that the people whom the data describe remain anonymous.”

## Slide 17: Data Logging Best Practices
To improve data credibility and reduce uncertainty:
  Minimize truncating or rounding of data
  Have sufficient memory for data storage
  Minimize access to data logs
  Ensure proper programming
  Double-check communication between sensors and logs
  Protect against tampering and the elements
  Perform routine verification activities

## Slide 18: Data Communication Best Practices
To improve data credibility and reduce uncertainty:
  Follow regulations and site specifications: safety for GSM and GPRS, cabling requirements, etc.
  Ensure high-quality communication: signal strength, cable connections, and as little throttling as possible
  Minimize access to communication equipment
  Protect against tampering and the elements
  Perform routine inspections and communication tests

## Slide 19: Data Storage Best Practices
To improve data credibility and reduce uncertainty:
  Keep backups separate from the primary data storage systems and use additional off-site backups when possible
  Use proven backup techniques and technologies
  Use backups that retain data in original format for at least five years
  Minimize access to data storage equipment
  Protect against tampering and the elements
  Perform routine inspections and backup tests

## Slide 20: Data Integration
Project Haystack /Brick
Building Energy Model-Sensor Data Integration for Energy-Flexible Buildings

## Slide 21: Data Calculation Best Practices
To improve data credibility and reduce uncertainty:
  Use the correct units for values
  Apply the correct equations
  Use correct conversion formulas

## Slide 22: Data Stipulation Best Practices
Note: A stipulation is “an assumption on which rests the validity or effect of something else.”
To improve data credibility and reduce uncertainty:
  Double-check validity of stipulations
  Obtain agreements about stipulations in writing

## Slide 23: Other Data Credibility Best Practices
Develop a quality management system in accordance with ISO Guidelines 9001 and 17020 and use, maintain, and whenever possible improve the quality management system.
Disclose full credibility assessment results to all relevant stakeholders, obtain agreement on acceptable levels of data credibility, and adhere to applicable M&V guidelines and protocols as well as the methodologies agreed upon for the purposes of the project.
ISO 9001: iso.org/files/live/sites/isoorg/files/store/en/PUB100080.pdf

## Slide 24: Calibration
Calibrating metering system components reduces unknown uncertainty factors.
Calibration should be performed by an accredited metrologist.
  Most accrediting bodies are affiliated with the International Laboratory Accreditation Cooperation (ILAC). These affiliations ensure that a metrologist’s accreditation meets global standards.
Notes: Instructor Note: Remember that calibration is meaningless if installation and setup are performed incorrectly. Data is useless if it comes from a meter that very accurately measures the wrong thing.
Useful Links
https://www.iso.org/ISO-IEC-17025-testing-and-calibration-laboratories.html
https://anab.ansi.org/standard/iso-iec-17025/

## Slide 25: Calibration Phases
There are two often confused phases in calibration:
  Knowing the error of the measurement instrument, sensor, or logger
  Adjusting or fine-tuning the measurement system component to achieve the least amount of error possible (also known as zeroing)

## Slide 26: When Is Calibration Necessary?
After calibration-altering event:
Portable equipment—bump, drop, poor storage, battery problem.
Permanent—power surge or spike, fire, etc.
Otherwise:
Portable equipment—Once every year if in weekly use or once every two years if in monthly (or less frequent) use
Permanent—Can remain calibrated for five years or more if properly installed and protected

## Slide 27: Calibration Verification
Calibration can be verified through an in-use calibration check. This is when a meter is used to measure a known load—such as a resistive heater—and its results are compared against those of a calibrated measurement system of known calibration status.
Portable metering systems of known calibration status can also be used to verify the collaboration of permanent metering systems.

## Slide 28: Data-Related Costs
When data is crucial, the data system becomes crucial as well.
Crucial data systems should have additional safety measures, backup features, and capacity to operate outside normal conditions.
All this comes at a cost.

## Slide 29: Indirect Data-Related Costs
There are also indirect costs associated with data loss.
Data lost due to metering or communication failure can mean …
  For the CMVP: wasted professional time, delays in deliverables, and increased rental fees
  For the client or other stakeholders: loss of productivity, loss of income, missed deadlines, incorrect invoicing, and even equipment or system damage

## Slide 30: Accounting for All Data-Related Costs
The cost of data consists of three parts:
  Material
  Communication
  Maintenance
Many account for material costs but fail to consider the costs associated with communication and maintenance.
The CMVP must budget for all data-related costs that accrue during the M&V assessment period.

## Slide 31: Safety
Only qualified individuals should install, operate, or handle metering systems—and only when permission to perform the work has been obtained.
Each type of metering installation, resource or material being measured, and environment has its own set of safety protocols and requirements. The CMVP must ensure that these are known, understood, and adhered to.
The CMVP may be held liable for any catastrophic events that occur in the course of M&V activities or in systems with M&V metering installed.

## Slide 32: Safety
As a result of failing to follow safety protocols and requirements, many have lost limbs, eyes, and even their lives while working on small, low-voltage distribution boards to install temporary metering.
Events can become particularly tragic when they involve work with steam, hot water, chemicals, pressurized materials, height, depth, extreme heat or cold, or moving parts.
Always coordinate with the proper site representatives.
If you ever have any concerns, have a specialist perform or assist in performing the work.

## Slide 33: OSHA
OSHA 3071
Asbestos

## Slide 34
The Future of Metering:
AMI 2.0 and Load Disaggregation
Advanced metering for modern M&V practice

## Slide 35
Traditional AMI vs. Next-Generation AMI 2.0
Traditional AMI 1.0
Next-Generation AMI 2.0
15-60 minute intervals
Basic energy + voltage data
Designed primarily for billing
Total building load only
Limited analytics capabilities
Example:
'Building used 45 kWh
from 2:00-3:00 PM'
Sub-second to millisecond sampling
Waveform capture (kHz range)
On-meter machine learning
Identifies individual loads (NILM)
Advanced fault detection
Example:
'HVAC: 8 kW, EV: 7 kW,
Water heater: 4 kW'
Key Capability: Non-Intrusive Load Monitoring (NILM) enables appliance-level M&V without sub-meters

## Slide 36
How Load Disaggregation Works
Three Approaches to Identifying Individual Loads
High-Frequency Waveform
Captures voltage + current at kHz
Analyzes harmonics, transients, spectral patterns
Most accurate approach
Research frontier
Edge-Computed
Machine learning runs on meter
Uses appliance libraries
Pattern recognition
Example: 'EV charging detected with 92% confidence'
Cloud-Assisted Hybrid
Low-freq continuous + high-freq bursts
Backend analytics
Where many CA pilots are
Balance accuracy vs. cost
Benefits for M&V Practice:
Enables retrofit isolation without expensive sub-metering infrastructure
Reduces M&V costs by 70-90% compared to traditional sub-metering
Provides appliance-level verification from main service meter
Identifies equipment faults and operational issues remotely

## Slide 37
Who Is Building This Technology
Key Commercial Vendors
Sense (home device → meter integration) Partnered with Landis+Gyr and Itron; high-frequency waveform analytics
Landis+Gyr Revelo (True AMI 2.0 platform) Applications run directly on meter; load disaggregation + DER visibility
Itron Intelis / Distributed Intelligence On-meter analytics; detects EV, solar, service quality, appliances
California Utility Adoption Status (2025)
SCE: Evaluating Distributed Intelligence (DI) and DER-aware meters; AMI 2.0 planning underway
SDG&E: Running EV detection pilots; strongest in DER visibility programs
PG&E: Exploring AMI 2.0 upgrade paths; meter refresh cycle approaching
SMUD (Sacramento): NILM pilots including Sense integration; focus on grid-interactive buildings
LADWP: AMI 2.0 rollout begins 2025 with load-identification capabilities

## Slide 38
Implications for M&V Practice
Four Ways AMI 2.0 Transforms Measurement and Verification
1. Event-Level M&V
Before: 15-minute interval kWh deltas
After: Heat pump cycle counts, EV charging sessions, compressor duty cycles
Benefit: Verify WHAT changed, not just that energy changed
2. DER Verification
Before: Separate meters required for solar, battery
After: Detect solar production, battery charge/discharge from main meter
Benefit: Reduce metering infrastructure costs
3. Load Flexibility Analytics
Before: Assume which loads are flexible
After: Identify actual flexible vs. inflexible loads
Benefit: Data-driven demand response strategies
4. Retrofit Isolation Without Sub-Meters
Before: Install sub-meters for each ECM ($15k-$25k)
After: Identify HVAC, lighting, equipment changes from main meter
Benefit: 70-90% reduction in M&V metering costs
Bottom Line: AMI 2.0 enables professional-grade M&V at a fraction of traditional metering costs

## Slide 39
What CMVPs Should Do Now
Current State (2025):
Most AMI still 15-60 minute intervals (AMI 1.0)
AMI 2.0 in pilot and early deployment phase
California leading adoption; other states following
Technology proven; costs declining with scale
Action Items for M&V Planning
✓ Ask utility: 'Do you have AMI 2.0 or high-resolution meters deployed?'
✓ Include AMI 2.0 in M&V cost-benefit analysis Example: Sub-metering ($25k) vs. Data access ($1.5k) = $23.5k savings
✓ Plan for granular data access in M&V plans Specify: Data resolution, load types, accuracy requirements, privacy protocols
✓ Learn NILM terminology: Non-Intrusive Load Monitoring, edge analytics, waveform capture, disaggregation confidence scores
✓ Follow California utility pilots and CPUC proceedings
Resources: CPUC AMI 2.0 filings | EPRI NILM reports | SCE/PG&E/SDG&E modernization plans | Vendor sites (Landis+Gyr, Itron, Sense)

## Slide 40: NFPA
NFPA 70E (2017): Standard for Electrical Safety in the Workplace
360 Training: NFPA 70E

## Slide 41: Scenario – Module 8
Please open your participant guide to the scenario for Module 8: Metering Considerations.

## Slide 42: Key Takeaways
Metering is at the core of M&V.
There are permanent as well as temporary (or portable) metering systems with various data communication capabilities.
Following best practices can improve data credibility and reduce uncertainty.
Calibrating metering system components reduces unknown uncertainty factors and should be performed by an accredited metrologist.
Only qualified individuals should install, operate, or handle metering systems—and only when permission to perform the work has been obtained.

## Slide 43: Module 8: Metering Considerations
What are the main criteria for selecting between permanent and portable metering systems in an M&V project?
How do calibration and verification processes improve the credibility of measured data in M&V?
Outline the potential costs and risks related to data logging, storage, and communication failures in metering systems