## Slide 1
How Much Should You
Spend on M&V?
An Uncertainty Budget Algorithm
for the Greenfield Municipal Center
Steve Kromer, P.E., CMVP #1 | Counterfactual Designs

## Slide 2
The Core Question
M&V costs money. Uncertainty costs money.
How do you allocate a limited budget to get the
greatest reduction in risk?
What You Spend
Meters & sensors
Data collection & analysis
Expert review & reporting
What You Get
Reduced settlement risk
Defensible savings claims
Informed decision-making

## Slide 3
The Uncertainty Budget Algorithm
1
Identify
List all sources of uncertainty:
aleatory, epistemic, ontological
▶
2
Quantify
Estimate cost & benefit of
each reduction action
▶
3
Optimize
Allocate $ where marginal
risk reduction is greatest
▶
4
Implement
Deploy meters, models,
and protocols
▶
5
Iterate
Update as new data
arrives; re-optimize
The Optimization Problem
Maximize: Σ Uncertainty_Reduction(i) subject to: Σ Cost(i) ≤ Budget
Allocate the next dollar where the marginal benefit-to-cost ratio is highest. Stop when the budget is exhausted.

## Slide 4
Greenfield Municipal Center — 4 ECMs
62,000 sq ft | Mid-Atlantic | 15-year ESPC | Combined savings: 122,390 kWh (10.5%)
ECM-1: LED Lighting
157,146 kWh
Retrofit Isolation
Key Parameter (Option A)
Uncertainty: LOW
Fixture wattage measured;
hours stipulated. Stable.
ECM-2: Chiller/DX
Combined w/ WF
Whole Facility
(Student decides)
Uncertainty: MEDIUM
COP from nameplate;
interactive effects present.
ECM-3: Roof Insulation
Combined w/ WF
Whole Facility
Inverse Model (Option C)
Uncertainty: HIGH
Cannot isolate. Only 12
monthly points for regression.
ECM-4: VFDs on AHUs
Varies w/ load
Retrofit Isolation
Continuous (Option B)
Uncertainty: MEDIUM
672 hourly points; fan law
validation. Load-dependent.

## Slide 5
Applying the Algorithm to Greenfield
M&V Action | ECM | Est. Cost | Uncertainty Reduced | Benefit/ Cost Ratio | Priority
Spot-measure LED wattage (620 fixtures, sampling plan) | ECM-1 | $2,000 | High (validates 157k kWh stipulation) | ★★★★★ | #1
Install 3 fan kW submeters (AHU-1, AHU-2, AHU-3) | ECM-4 | $8,000 | High (continuous verification of variable-load savings) | ★★★★ | #2
Whole-facility utility meters (12-month baseline regression) | ECM-2,3 | $3,000 | Medium (model uncertainty remains; only 12 monthly points) | ★★★ | #3
NRA protocol for data center expansion (expert judgment) | All | $5,000 | Critical (masks 100k kWh of true savings without it) | ★★★★★ | #1*
Additional interval metering (15-min electric data) | ECM-2,3 | $12,000 | Low-Medium (more data points but diminishing returns) | ★★ | #4
* NRA protocol is #1 by impact: without it, data center expansion hides ~100,000 kWh of true savings.

## Slide 6
Diminishing Returns — Where to Stop
Chart: 
| $0 | $2k | $5k | $10k | $18k | $25k | $30k
Uncertainty Remaining (%) | 100 | 72 | 45 | 28 | 18 | 15 | 13
$2k
LED spot measurements
eliminate stipulation risk
$10k
Fan submeters + regression
cover 80% of uncertainty
$18k
NRA protocol ensures
data center doesn't mask savings
$30k+
Diminishing returns.
Additional spend adds little.

## Slide 7
Three Uncertainty Types → Three Strategies
Aleatory
Irreducible randomness
Investment Strategy:
More data points.
Longer baselines.
Better statistical models.
In Greenfield:
statssheets residuals;
mv-workbench diagnostics;
12-month baseline regression
mv-workbench
Epistemic
Reducible by better knowledge
Investment Strategy:
Better instruments.
Submetering.
Bayesian updating.
Expert analysis.
In Greenfield:
LED spot measurement;
VFD continuous metering;
bayesian-mv-module posteriors
bayesian-mv-module
Ontological
World doesn't fit your model
Investment Strategy:
NRA protocols.
Scenario planning.
Contingency reserves.
Professional judgment.
In Greenfield:
Data center expansion;
entropy-audit-tool Critical zones;
CMVP_JTA governance
entropy-audit-tool

## Slide 8
Key Takeaways
1
M&V spending follows diminishing returns. The first $10k eliminates ~70% of uncertainty. After $20k, you're polishing.
2
Prioritize by marginal benefit-to-cost ratio, not by ECM size. The NRA protocol ($5k) may be the single highest-value investment.
3
Match the investment to the uncertainty type. Don't spend on better meters when the real risk is ontological (the world changing on you).
4
The counterfactual is a designed artifact. Your M&V budget is the construction budget for that artifact.
counterfactual-designs.com | cmvp-capstone.vercel.app | mnvexample.streamlit.app