## Index
Greenfield Municipal Center — Offline Data Package
CMVP Capstone Project · Use this workbook when the web app is unavailable
Tab | Sheet Name | Purpose | Used On
1 | Index | This page | —
2 | Scenario | Building overview, ECM descriptions, contract terms | Day 1
3 | Baseline Monthly | 12-month baseline utility data + scatter plot data | Day 1–2
4 | Reporting Monthly | 12-month reporting period data (with NRA event) | Day 2–3
5 | No-NRA Monthly | Reporting data without data center expansion (reference) | Day 2
6 | Scatter Plots | OAT vs kWh / therms — ready for regression analysis | Day 2
7 | Model Results | Pre-computed 5P model statistics and change points | Day 2
8 | Lighting Calc | ECM-1 stipulation calculator — editable hours | Day 2
9 | Fan Law Calc | ECM-4 VFD fan law calculator + pre/post spot data | Day 2
10 | Savings Calc | Monthly savings, valuation, CO₂ (formula-driven) | Day 3
11 | NRA Summary | Data center NRA — evidence and adjustment protocol | Day 2–3

## Scenario
Greenfield Municipal Center — Scenario Overview
ESPC Contract · Mid-Atlantic Climate · 62,000 sq ft
BUILDING DESCRIPTION
Location | Mid-Atlantic region (heating-dominant; significant summer cooling)
Total Area | 62,000 sq ft
Contract Type | Energy Savings Performance Contract (ESPC)
Baseline Period | Year 1 (12 months, Jan–Dec)
Reporting Period | Year 2 (12 months, Jan–Dec)
WINGS / SPACES
Wing A | Office space — 35,000 sq ft, standard HVAC, Mon–Fri hours
Wing B | Public library & community rooms — 15,000 sq ft, extended hours
Wing C | Data center / IT — 2,000 sq ft, 24/7 constant load
Common Areas | Lobby, corridors, mechanical rooms — 10,000 sq ft
UTILITY RATES (for savings valuation)
Electricity | $0.105/kWh (flat blended rate)
Natural Gas | $1.15/therm
CO₂ EMISSION FACTORS
Electricity | 0.417 kg CO₂/kWh (mid-Atlantic grid average)
Natural Gas | 5.302 kg CO₂/therm
ECM SUMMARY
ECM | Description | Expected Elec Savings (kWh/yr) | Expected Gas Savings (therms/yr) | M&V Approach | Approach Type | Domain
ECM-1 | LED lighting + occupancy controls (Wings A & B) | 258,000 | — | Retrofit Isolation | Stipulated (Option A) | Domain 3
ECM-2 | Chiller replacement (central plant) | 150,000 | — | Whole Facility or Retrofit Isolation | Student Decision | Domain 2, 4
ECM-3 | Building envelope — roof insulation | ~60,000 | ~1,200 | Whole Facility | Option C | Domain 4
ECM-4 | VFDs on AHU supply fans (3 units) | 85,000 | — | Retrofit Isolation | Continuous (Option B) | Domain 3

## Baseline Monthly
Baseline Period — Monthly Utility Data
12 months · Pre-retrofit · No ECMs installed
Month | Days | Avg OAT (°F) | Total kWh | Total Therms | Lighting (kWh) | Cooling (kWh) | Fan (kWh) | Plug (kWh) | Data Center (kWh) | Heating (therms) | DHW (therms)
Jan | 31 | 33 | 108662 | 1139 | 14904 | 10061 | 11002 | 14140 | 37274 | 889 | 250
Feb | 28 | 34.9 | 93429 | 779 | 13225 | 9114 | 9442 | 12598 | 33667 | 545 | 234
Mar | 31 | 45.9 | 93584 | 482 | 14293 | 11136 | 9997 | 13692 | 37274 | 338 | 145
Apr | 30 | 54.4 | 89039 | 343 | 14345 | 12492 | 9829 | 13626 | 36072 | 240 | 103
May | 31 | 64.7 | 95784 | 270 | 14904 | 18641 | 10233 | 14140 | 37274 | 54 | 216
Jun | 30 | 72.5 | 95115 | 223 | 13734 | 22395 | 9676 | 13178 | 36072 | 45 | 179
Jul | 31 | 76.1 | 104702 | 237 | 14904 | 28107 | 10270 | 14140 | 37274 | 47 | 190
Aug | 31 | 73.4 | 100216 | 237 | 14682 | 24007 | 10242 | 13970 | 37274 | 47 | 189
Sep | 30 | 68.2 | 92868 | 236 | 13956 | 19542 | 9693 | 13347 | 36072 | 47 | 189
Oct | 31 | 53.5 | 92756 | 366 | 14904 | 13037 | 10174 | 14140 | 37274 | 256 | 110
Nov | 30 | 46.1 | 90863 | 488 | 14123 | 10245 | 9838 | 13456 | 36072 | 342 | 146
Dec | 31 | 33.8 | 105610 | 1001 | 14515 | 9915 | 10581 | 13861 | 37274 | 751 | 250
TOTAL / AVG | 365 | 54.7083 | 1162628 | 5801 | 172489 | 188692 | 120977 | 164288 | 438873 | 3601 | 2201
NOTE: Total kWh and Total Therms are the whole-facility independent variables used to fit the baseline model. Avg OAT is the primary independent variable. Subsystem columns (Lighting, Cooling, etc.) are provided for reference only — they are not available from utility bills in a real project.

## Reporting Monthly
Reporting Period — Monthly Utility Data (with NRA Event)
12 months · Post-retrofit · NRA: Data center expansion begins Month 8
Month | Days | Avg OAT (°F) | Total kWh | Total Therms | Lighting (kWh) | Cooling (kWh) | Fan (kWh) | Plug (kWh) | Data Center (kWh) | Heating (therms) | DHW (therms)
Jan | 31 | 33 | 100821 | 1161 | 9664 | 9957 | 7257 | 14140 | 37274 | 911 | 250
Feb | 28 | 34.9 | 86657 | 857 | 8593 | 9007 | 6406 | 12598 | 33667 | 607 | 250
Mar | 31 | 45.9 | 85854 | 540 | 9315 | 10566 | 6898 | 13692 | 37274 | 378 | 162
Apr | 30 | 54.4 | 80327 | 380 | 9307 | 11171 | 6758 | 13626 | 36072 | 266 | 114
May | 31 | 64.7 | 83786 | 281 | 9664 | 14872 | 7022 | 14140 | 37274 | 56 | 225
Jun | 30 | 72.5 | 82013 | 225 | 8958 | 17024 | 6680 | 13178 | 36072 | 45 | 180
Jul | 31 | 76.1 | 88744 | 238 | 9664 | 20615 | 7040 | 14140 | 37274 | 48 | 190
Aug | 31 | 73.4 | 105103 | 238 | 10433 | 21526 | 7026 | 13903 | 52154 | 48 | 191 | ◄ NRA: Data center expansion
Sep | 30 | 68.2 | 99247 | 240 | 9938 | 18509 | 6690 | 13282 | 50472 | 48 | 192
Oct | 31 | 53.5 | 102576 | 400 | 10553 | 14910 | 6990 | 14072 | 52154 | 280 | 120
Nov | 30 | 46.1 | 101922 | 548 | 10048 | 13081 | 6754 | 13391 | 50472 | 384 | 164
Dec | 31 | 33.8 | 117172 | 1049 | 10323 | 13129 | 7092 | 13794 | 52154 | 799 | 250
TOTAL / AVG | 365 | 54.7083 | 1134222 | 6157 | 116460 | 174367 | 82613 | 163956 | 512313 | 3870 | 2288
SHADED ROWS (Months 8–12): Data center expansion adds ~14,880 kWh/month above what the baseline model predicts. This is the Non-Routine Adjustment (NRA) event. Without adjustment, these months show negative savings.

## No-NRA Monthly
Reporting Period — No NRA Scenario (Reference Only)
Same weather, same retrofits — but data center load stays at baseline level
Month | Days | Avg OAT (°F) | Total kWh | Total Therms
Jan | 31 | 33 | 100821 | 1161
Feb | 28 | 34.9 | 86657 | 857
Mar | 31 | 45.9 | 85854 | 540
Apr | 30 | 54.4 | 80327 | 380
May | 31 | 64.7 | 83786 | 281
Jun | 30 | 72.5 | 82013 | 225
Jul | 31 | 76.1 | 88744 | 238
Aug | 31 | 73.4 | 85883 | 238
Sep | 30 | 68.2 | 80749 | 240
Oct | 31 | 53.5 | 83597 | 400
Nov | 30 | 46.1 | 83585 | 548
Dec | 31 | 33.8 | 98222 | 1049
This is the counterfactual without the data center expansion NRA. Comparing this to 'Reporting Monthly' isolates exactly the NRA effect. Students: why do months 8–12 differ from the 'Reporting Monthly' tab?

## Scatter Plots
Scatter Plot Data — OAT vs. Energy Use
Use this data to create scatter plots and fit regression models
Baseline Month | Avg OAT (°F) | Total kWh (Baseline) | Total Therms (Baseline) | Reporting Month | Avg OAT (°F) | Total kWh (Reporting) | Total Therms (Reporting)
Jan | 33 | 108662 | 1139 | Jan | 33 | 100821 | 1161
Feb | 34.9 | 93429 | 779 | Feb | 34.9 | 86657 | 857
Mar | 45.9 | 93584 | 482 | Mar | 45.9 | 85854 | 540
Apr | 54.4 | 89039 | 343 | Apr | 54.4 | 80327 | 380
May | 64.7 | 95784 | 270 | May | 64.7 | 83786 | 281
Jun | 72.5 | 95115 | 223 | Jun | 72.5 | 82013 | 225
Jul | 76.1 | 104702 | 237 | Jul | 76.1 | 88744 | 238
Aug | 73.4 | 100216 | 237 | Aug | 73.4 | 105103 | 238
Sep | 68.2 | 92868 | 236 | Sep | 68.2 | 99247 | 240
Oct | 53.5 | 92756 | 366 | Oct | 53.5 | 102576 | 400
Nov | 46.1 | 90863 | 488 | Nov | 46.1 | 101922 | 548
Dec | 33.8 | 105610 | 1001 | Dec | 33.8 | 117172 | 1049
HOW TO USE: (1) Select columns B & C (OAT vs kWh) for a baseline electric scatter plot. (2) Select columns B & D (OAT vs Therms) for a baseline gas scatter plot. (3) Insert > Chart > X-Y Scatter. (4) Add a trendline. Observation: Does the electric plot look linear? Where are the inflection points?

## Model Results
Baseline Model Results — Pre-Computed Statistics
5-Parameter Change-Point Model · ASHRAE Guideline 14 Validation
ELECTRIC MODEL (5-Parameter Change-Point)
Model Type | 5P — Heating + Cooling change-point
Heating Change Point (CP1) | 48 °F [auto-fit optimal: 35 °F — see Teaching Moment 1]
Cooling Change Point (CP2) | 63 °F [auto-fit optimal: 71 °F — see Teaching Moment 1]
Baseline (intercept) | 37,274 kWh/month
Heating Slope | −2,087 kWh/°F·month (below CP1)
Cooling Slope | +1,664 kWh/°F·month (above CP2)
R² (coefficient of determination) | 0.91 (physically constrained) / 0.95 (auto-fit)
CV(RMSE) | 5.1% (physically constrained) / 3.8% (auto-fit)
NMBE | 0.3%
Guideline 14 — CV(RMSE) ≤ 15%? | ✓ PASS
Guideline 14 — NMBE ≤ 5%? | ✓ PASS
GAS MODEL (3-Parameter Heating)
Model Type | 3P — Heating change-point only
Heating Change Point | 57 °F
Baseline (intercept) | 47 therms/month (DHW baseload)
Heating Slope | −36.1 therms/°F·month (below change point)
R² | 0.97
CV(RMSE) | 16.1% ← EXCEEDS G14 threshold of 15% [Teaching Moment 2]
NMBE | 1.2%
Guideline 14 — CV(RMSE) ≤ 15%? | ✗ FAIL — discuss: is this model still usable?
Guideline 14 — NMBE ≤ 5%? | ✓ PASS
★ TEACHING MOMENT 1 — Physics vs. Statistics
The auto-fit algorithm finds change points at 35/71°F (R²=0.95) because they minimize residuals mathematically. But 35°F as a cooling balance point is physically unrealistic — no building switches to mechanical cooling at 35°F. The physically constrained model (48/63°F, R²=0.91) sacrifices statistical fit for interpretability. Which would you report? Why?

## Lighting Calc
ECM-1 Lighting Stipulation Calculator
Key Parameter Measurement (cf. IPMVP Option A) · Blue cells are editable
# | Space | Fixture Qty | Baseline (W/fixture) | Retrofit (W/fixture) | ΔW (W/fixture) | Annual Hours (editable) | kWh Saved
1 | Wing A — Open Office (2nd floor) | 120 | 128 | 40 | 88 | 2860 | 30201.6
2 | Wing A — Open Office (1st floor) | 120 | 128 | 40 | 88 | 2860 | 30201.6
3 | Wing A — Private Offices | 80 | 96 | 32 | 64 | 2600 | 13312
4 | Wing A — Conference Rooms | 40 | 128 | 40 | 88 | 1200 | 4224
5 | Wing A — Corridors & Restrooms | 60 | 64 | 20 | 44 | 3380 | 8923.2
6 | Wing B — Reading Rooms | 100 | 128 | 40 | 88 | 3900 | 34320
7 | Wing B — Stacks | 150 | 96 | 32 | 64 | 2600 | 24960
8 | Wing B — Meeting Rooms | 30 | 128 | 40 | 88 | 1500 | 3960
9 | Wing B — Circulation & Entry | 40 | 64 | 20 | 44 | 4160 | 7321.6
| TOTAL | 740 |  |  |  |  | 157424
INSTRUCTIONS: Annual Hours (column G, blue) are stipulated values. Change them to test different schedule assumptions. What is your basis for each value? Typical ranges: offices 2,500–3,000 hrs; libraries/extended hours 3,500–4,500 hrs; corridors (always on) 3,000–4,000 hrs.
★ TEACHING MOMENT 4 — Interactive Effects: This stipulation calculates ECM-1 savings in isolation. The whole-facility model (Savings Calc tab) shows different total savings because less lighting waste heat → less summer cooling load (good) but more winter heating load (bad). The stipulation does NOT capture these interactive effects.

## Fan Law Calc
ECM-4 VFD Fan Law Calculator
Continuous Performance Verification · Fan Law: Power ∝ Speed³
FAN LAW RELATIONSHIP
Affinity Law | P₂/P₁ = (N₂/N₁)³ where P = power (kW) and N = speed (%)
Implication | A 10% speed reduction → 27% power reduction (not 10%)
Implication | A 35% speed reduction → 72.6% power reduction
AHU NAMEPLATE DATA (Pre-VFD)
AHU-1 (Wing A) | Design: 100% speed = 8.85 kW, 15,000 CFM
AHU-2 (Wing B/C) | Design: 100% speed = 4.72 kW, 8,000 CFM
AHU-3 (Common Areas) | Design: 100% speed = 2.68 kW, 5,000 CFM
FAN LAW CALCULATOR — Edit speed reduction to see power impact
AHU | Baseline Power (kW) | Speed Reduction (%) [EDIT THIS] | New Speed (%) | Fan Law Factor | New Power (kW) | Power Saved (kW)
AHU-1 | 8.85 | 35 | 65 | 0.27463 | 2.4304 | 6.4196
AHU-2 | 4.72 | 35 | 65 | 0.27463 | 1.2962 | 3.4238
AHU-3 | 2.68 | 35 | 65 | 0.27463 | 0.736 | 1.944
SAMPLE SPOT MEASUREMENTS — Pre/Post VFD (March 15, Operating Hours)
Hour | OAT (°F) | AHU-1 Pre (kW) | AHU-1 Post (kW) | AHU-1 Speed % | AHU-2 Pre (kW) | AHU-2 Post (kW) | AHU-2 Speed % | AHU-3 Pre (kW) | AHU-3 Post (kW)
08:00 | 29.9 | 8.85 | 4.42 | 100 | 4.72 | 2.36 | 100 | 2.68 | 1.33
09:00 | 37.7 | 8.85 | 3.93 | 89 | 4.72 | 2.1 | 89 | 2.68 | 1.21
10:00 | 43.1 | 8.85 | 3.36 | 76 | 4.72 | 1.79 | 76 | 2.68 | 1.06
11:00 | 47.4 | 8.85 | 2.89 | 65 | 4.72 | 1.54 | 65 | 2.68 | 0.95
12:00 | 50.3 | 8.85 | 2.59 | 59 | 4.72 | 1.38 | 59 | 2.68 | 0.87
13:00 | 51.1 | 8.85 | 2.5 | 57 | 4.72 | 1.34 | 57 | 2.68 | 0.85
14:00 | 53.6 | 8.85 | 2.24 | 51 | 4.72 | 1.2 | 51 | 2.68 | 0.78
15:00 | 55.6 | 8.85 | 2.02 | 46 | 4.72 | 1.08 | 46 | 2.68 | 0.73
★ TEACHING MOMENT 5 — Fan Law: Notice AHU-1 at 09:00 drops from 8.85 kW (pre) to 3.93 kW (post) when speed is 89%. Fan law predicts: 0.89³ = 0.705 → 8.85 × 0.705 = 6.23 kW. Actual is lower because VAV dampers further reduce load. Key insight: small speed errors → large power errors. Continuous metering is better than spot measurement.

## Savings Calc
Savings Calculator — Whole-Facility Method
Formula-driven · Uses 5P electric model + 3P gas model coefficients from Model Results tab
MODEL ASSUMPTIONS (editable — blue cells)
Electricity rate ($/kWh) | 0.105
Gas rate ($/therm) | 1.15
Elec CO₂ factor (kg/kWh) | 0.417
Gas CO₂ factor (kg/therm) | 5.302
Electric CP1 — heating (°F) | 48
Electric CP2 — cooling (°F) | 63
Elec baseline intercept (kWh/mo) | 37274
Elec heating slope (kWh/°F) | -2087
Elec cooling slope (kWh/°F) | 1664
Gas CP — heating (°F) | 57
Gas baseline intercept (therms/mo) | 47
Gas heating slope (therms/°F) | -36.1
NRA adjustment (kWh/month, months 8-12) | 14880
MONTHLY SAVINGS TABLE
Month | Actual kWh | Actual Therms | OAT (°F) | Predicted kWh (model) | Predicted Therms | NRA Adj (kWh) | Elec Savings (kWh) | Gas Savings (therms) | Notes
Jan | 100821 | 1161 | 33 | 68579 | 913.4 | 0 | -32242 | -247.6
Feb | 86657 | 857 | 34.9 | 64613.7 | 844.81 | 0 | -22043.3 | -12.19
Mar | 85854 | 540 | 45.9 | 41656.7 | 447.71 | 0 | -44197.3 | -92.29
Apr | 80327 | 380 | 54.4 | 37274 | 140.86 | 0 | -43053 | -239.14
May | 83786 | 281 | 64.7 | 40102.8 | 47 | 0 | -43683.2 | -234
Jun | 82013 | 225 | 72.5 | 53082 | 47 | 0 | -28931 | -178
Jul | 88744 | 238 | 76.1 | 59072.4 | 47 | 0 | -29671.6 | -191
Aug | 105103 | 238 | 73.4 | 54579.6 | 47 | 14880 | -35643.4 | -191 | ★ NRA: Data center expansion
Sep | 99247 | 240 | 68.2 | 45926.8 | 47 | 14880 | -38440.2 | -193 | ★ NRA: Data center expansion
Oct | 102576 | 400 | 53.5 | 37274 | 173.35 | 14880 | -50422 | -226.65 | ★ NRA: Data center expansion
Nov | 101922 | 548 | 46.1 | 41239.3 | 440.49 | 14880 | -45802.7 | -107.51 | ★ NRA: Data center expansion
Dec | 117172 | 1049 | 33.8 | 66909.4 | 884.52 | 14880 | -35382.6 | -164.48 | ★ NRA: Data center expansion
ANNUAL TOTAL | [6 empty] | -449512.3 | -2076.86
Item | Quantity | Rate | Value ($) | Notes
Electricity savings | -449512.3 | 0.105 | -47198.7915 | kWh × $/kWh
Gas savings | -2076.86 | 1.15 | -2388.389 | therms × $/therm
TOTAL VALUE |  |  | -49587.1805
Elec CO₂ savings | -449512.3 | 0.000417 | -187.4466 | kWh × metric tons/kWh
Gas CO₂ savings | -2076.86 | 0.005302 | -11.0115 | therms × metric tons/therm
TOTAL CO₂ (metric tons) |  |  | -198.4581

## NRA Summary
Non-Routine Adjustment — Data Center Expansion
Teaching Moment 3 · Evidence, Quantification, and Reporting Protocol
NRA EVENT DESCRIPTION
Event | Data center / IT operations expansion in Wing C
Detection | Step change in electric consumption visible in Time Series chart starting Month 8
Month of onset | Month 8 (August of reporting year)
Affected months | Months 8–12 (5 months)
Approximate magnitude | ~14,880 kWh/month above model prediction
Annual NRA total (Months 8–12) | ~74,400 kWh
EVIDENCE REQUIRED
Primary evidence | IT asset inventory showing expanded server rack count and UPS load
Supporting evidence 1 | Facilities work order or change order for Wing C expansion
Supporting evidence 2 | Sub-meter data from Wing C data center panel (if available)
Supporting evidence 3 | IT department written confirmation of expansion date and load
WITHOUT NRA ADJUSTMENT
Months 8–12 apparent savings | NEGATIVE — project appears to have failed
Annual savings (unadjusted) | Reduced by ~74,400 kWh (~22% of expected savings)
Contract risk | ESCO may face penalty payment despite actual retrofit performance
WITH NRA ADJUSTMENT
Calculation | Reported savings = Model prediction − Actual + NRA adjustment
Adjusted annual savings | See Savings Calc tab with NRA applied
Contractual result | Savings verified; NRA documented and agreed by all parties
IPMVP REFERENCE
Protocol | IPMVP Section 4.2 — Non-Routine Adjustments
Requirement | NRAs must be agreed in advance in the M&V Plan or negotiated promptly
Documentation | NRA event, date, magnitude, evidence, and calculation method